## cost_matrix1
| label | costs_total | costs_om_total | costs_investment_over_lifetime | costs_upfront_in_year_zero | Replacement_costs_during_project_lifetime | costs_dispatch | costs_cost_om | annuity_total | annuity_om | levelized_cost_of_energy_of_asset
0 | ESS Li-Ion storage capacity | 11446783.3959 | 81243.3368 | 11365540.0591 | 9295377 | 2070163.0591 | 0 | 81243.3368 | 982254.4037 | 6971.5328 | 0.01093
0 | ESS Li-Ion input power | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
0 | ESS Li-Ion output power | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
0 | Charge Contoller ESS Li-Ion (charge) | 624768.2252 | 0 | 624768.2252 | 358452.0984 | 266316.1268 | 0 | 0 | 53611.6845 | 0 | 0.00646
0 | Charge Contoller ESS Li-Ion (discharge) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
0 | Solar inverter | 3908814.4242 | 1008712.997 | 2900101.4272 | 2163954.6 | 736146.8272 | 0 | 1008712.997 | 335417.3875 | 86558.184 | 0.00961
0 | Electricity grid_consumption_period | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
0 | PV si | 50958911.6343 | 19564540.7633 | 31394370.871 | 31394370.871 | 0 | 0 | 19564540.7633 | 4372810.5643 | 1678843.3621 | 0.11838
0 | Electricity grid_consumption_source | 81142029.7219 | 81142029.7219 | 0 | 0 | 0 | 81142029.7219 | 0 | 6962839.5388 | 6962839.5388 | 0.3088
0 | Electricity demand | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
0 | ESS Li-Ion bus_excess_sink | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
0 | Electricity bus_excess_sink | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
0 | PV bus_excess_sink | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
0 | Electricity grid_feedin_sink_sink | -7583336.1842 | -7583336.1842 | 0 | 0 | 0 | -7583336.1842 | 0 | -650730.0002 | -650730.0002 | -0.1

## scalar_matrix1
| label | unit | installedCap | optimizedAddCap | total_flow | annual_total_flow | peak_flow | average_flow | Total emissions
0 | ESS Li-Ion storage capacity | kWh | 0 | 46476.885 | 89908388.8706 | 89908388.8706 | 37181.508 | 10263.5147
0 | ESS Li-Ion input power | kW | 0 | 46476.885 | 8238507.0414 | 8238507.0414 | 8146.6386 | 940.4688
0 | ESS Li-Ion output power | kW | 0 | 46476.885 | 6673190.7104 | 6673190.7104 | 10353.038 | 761.7798
0 | Charge Contoller ESS Li-Ion (charge) | kW | 0 | 8146.6386 | 8305407.9807 | 8305407.9807 | 8146.6386 | 948.1059
0 | Charge Contoller ESS Li-Ion (discharge) | kW | 0 | 10353.038 | 6740091.6496 | 6740091.6496 | 10353.038 | 769.4168
0 | Solar inverter | kW | 0 | 21639.546 | 34886799.0541 | 34886799.0541 | 21639.546 | 3982.5113
0 | Electricity grid_consumption_period | ? | 0 | 10388.14 | 22548055.5012 | 22548055.5012 | 10388.14 | 2573.9789
0 | PV si | kWp | 0 | 33576.8672 | 36937825.3906 | 36937825.3906 | 27402.746 | 4216.6467 | 0
0 | Electricity grid_consumption_source | ? | 0 | 10388.14 | 22548055.5012 | 22548055.5012 | 10388.14 | 2573.9789 | 7621242.7594
0 | Electricity demand | kW | 0 | 0 | 49362238.1674 | 49362238.1674 | 10388.1396 | 5634.9587
0 | ESS Li-Ion bus_excess_sink | ? | 0 | 0 | 0 | 0 | 0 | 0
0 | Electricity bus_excess_sink | ? | 0 | 0 | 0 | 0 | 0 | 0
0 | PV bus_excess_sink | ? | 0 | 4624.2765 | 214879.0481 | 214879.0481 | 4624.2765 | 24.5296
0 | Electricity grid_feedin_sink_sink | ? | 0 | 15894.23 | 6507300.0022 | 6507300.0022 | 15894.23 | 742.8425

## scalars1
| 0 | unit
Attributed costsElectricity | 140497971.2175 | EUR
Degree of autonomy | 0.7483 | EUR
Degree of NZE | 1
Levelized costs of electricity equivalent | 0.24424 | EUR
Levelized costs of electricity equivalentElectricity | 0.24424 | EUR
Onsite energy fraction | 0.82383 | NA
Onsite energy matching | 0.61212 | EUR
Renewable factor | 0.65886 | EUR
Renewable share of local generation | 1 | EUR/year
Replacement_costs_during_project_lifetime | 3072626.0132 | EUR/year
Specific emissions per electricity equivalent | 0.15439 | NA
Total emissions | 7621242.7594 | NA
Total internal generation | 36937825.3906 | NA
Total internal non-renewable generation | 0 | NA
Total internal renewable generation | 36937825.3906 | NA
Total non-renewable energy use | 20293249.9511 | NA
Total renewable energy use | 39192630.9407 | NA
Total_demandElectricity | 49362238.1674 | NA
Total_demandElectricity_electricity_equivalent | 49362238.1674 | NA
Total_demand_electricity_equivalent | 49362238.1674 | NA
Total_excessElectricity | 214879.0481 | NA
Total_excessElectricity_electricity_equivalent | 214879.0481 | NA
Total_excess_electricity_equivalent | 214879.0481 | NA
Total_feedinElectricity | 6507300.0022 | NA
Total_feedinElectricity_electricity_equivalent | 6507300.0022 | NA
Total_feedin_electricity_equivalent | 6507300.0022 | NA
annuity_om | 8084482.6174 | NA
annuity_total | 12056203.5786 | NA
costs_cost_om | 20654497.0971 | NA
costs_dispatch | 73558693.5378 | NA
costs_investment_over_lifetime | 46284780.5826 | NA
costs_om_total | 94213190.6349 | NA
costs_total | 140497971.2175 | NA
costs_upfront_in_year_zero | 43212154.5694 | NA

## KPI individual sectors
| Renewable factor | Renewable share of local generation | Total internal non-renewable generation | Total internal non-renewable generation_electricity_equivalent | Total internal renewable generation | Total internal renewable generation_electricity_equivalent | Total non-renewable energy use | Total non-renewable energy use_electricity_equivalent | Total renewable energy use | Total renewable energy use_electricity_equivalent
0 | {'Electricity': 0.6588560235328053} | {'Electricity': 1.0} | {'Electricity': 0} | {'Electricity': 0} | {'Electricity': 36937825.39060506} | {'Electricity': 36937825.39060506} | {'Electricity': 20293249.951086923} | {'Electricity': 20293249.951086923} | {'Electricity': 39192630.94072583} | {'Electricity': 39192630.94072583}